## conductors
Conductor Spec | Name | Size | Cond Strand | Core Strand | Cond Wire Diameter | Cond Wire Diameter Units | Core Wire Diameter | Core Wire Diameter Units | Core OD | Core OD Units | Metal OD | Metal OD Units | Strand Lay | TW Type | TW Layers | low resistance temperature | resistance temperature units | high resistance temperature | low resistance Ω/unit | high resistance Ω/unit | resistance distance | resistance distance units | Al Weight | St Weight | Cu Weight | Alw Weight | specific heat weight unit | Values from
AAAC | Greeley | 927.2 | 37 |  | 0.1583 | in |  |  |  | in | 1.108 | in |  |  |  | 25 | C | 75 | 0.1193 | 0.1389 | 5280 | feet | 864.6 |  |  |  | J/(lb-C) | Southwire
AAC | Marigold | 1113 | 61 |  | 0.1351 | in |  |  |  | in | 1.216 | in |  |  |  | 25 | C | 75 | 0.0872 | 0.1032 | 5280 | feet | 1044 |  |  |  | J/(lb-C) | Southwire
ACSR | Turbit | 795 | 20 | 7 | 0.1994 | in | 0.0886 | in | 0.2658 | in | 1.0634 | in |  |  |  | 25 | C | 75 | 0.1185 | 0.1412 | 5280 | feet | 749 | 146.1 |  |  | J/(lb-C) | Southwire
ACSR | Puffin | 795 | 22 | 7 | 0.1901 | in | 0.1056 | in | 0.3168 | in | 1.0772 | in |  |  |  | 25 | C | 75 | 0.1179 | 0.1405 | 5280 | feet | 748.8 | 207.6 |  |  | J/(lb-C) | Southwire
ACSR | Cuckoo | 795 | 24 | 7 | 0.182 | in | 0.1213 | in | 0.3639 | in | 1.092 | in |  |  |  | 25 | C | 75 | 0.1172 | 0.1398 | 5280 | feet | 748.8 | 273.9 |  |  | J/(lb-C) | Southwire
ACSR | Drake | 795 | 26 | 7 | 0.1749 | in | 0.136 | in | 0.408 | in | 1.108 | in |  |  |  | 25 | C | 75 | 0.117 | 0.139 | 5280 | feet | 749.1 | 344.3 |  |  | J/(lb-C) | Ratekit
ACSR | Skimmer | 795 | 30 | 7 | 0.1628 | in | 0.1628 | in | 0.4884 | in | 1.14 | in |  |  |  | 25 | C | 75 | 0.1155 | 0.1379 | 5280 | feet | 750.7 | 493.3 |  |  | J/(lb-C) | Southwire
ACSR | Mallard | 795 | 30 | 19 | 0.1628 | in | 0.0977 | in | 0.4885 | in | 1.14 | in |  |  |  | 25 | C | 75 | 0.116 | 0.138 | 5280 | feet | 750.7 | 483.2 |  |  | J/(lb-C) | Ratekit
ACSR | Coot | 795 | 36 | 1 | 0.1486 | in | 0.1486 | in | 0.1486 | in | 1.04 | in |  |  |  | 25 | C | 75 | 0.119 | 0.1417 | 5280 | feet | 745.1 | 58.5 |  |  | J/(lb-C) | Southwire
ACSR | Tern | 795 | 45 | 7 | 0.1329 | in | 0.0886 | in | 0.2658 | in | 1.063 | in |  |  |  | 25 | C | 75 | 0.1185 | 0.1421 | 5280 | feet | 748.6 | 146.1 |  |  | J/(lb-C) | Southwire
ACSR | Condor | 795 | 54 | 7 | 0.1213 | in | 0.1213 | in | 0.3639 | in | 1.092 | in |  |  |  | 25 | C | 75 | 0.117 | 0.14 | 5280 | feet | 748.4 | 273.9 |  |  | J/(lb-C) | Ratekit
ACSR | Ruddy | 900 | 45 | 7 | 0.1414 | in | 0.0943 | in | 0.2829 | in | 1.131 | in |  |  |  | 25 | C | 75 | 0.1051 | 0.1259 | 5280 | feet | 847.4 | 165.5 |  |  | J/(lb-C) | Southwire
ACSR | Canary | 900 | 54 | 7 | 0.1291 | in | 0.1291 | in | 0.3873 | in | 1.162 | in |  |  |  | 25 | C | 75 | 0.1039 | 0.1269 | 5280 | feet | 847.7 | 310.2 |  |  | J/(lb-C) | Southwire
ACSR | Corncrake | 954 | 20 | 7 | 0.2184 | in | 0.0971 | in | 0.291 | in | 1.165 | in |  |  |  | 25 | C | 75 | 0.0994 | 0.1183 | 5280 | feet | 898.5 | 175.5 |  |  | J/(lb-C) | Southwire
ACSR | Redbird | 954 | 24 | 7 | 0.1994 | in | 0.1329 | in | 0.399 | in | 1.196 | in |  |  |  | 25 | C | 75 | 0.0982 | 0.117 | 5280 | feet | 898.8 | 328.7 |  |  | J/(lb-C) | Southwire
ACSR | Merganser | 954 | 30 | 7 | 0.1783 | in | 0.1783 | in | 0.5349 | in | 1.2481 | in |  |  |  | 25 | C | 75 | 0.0967 | 0.1152 | 5280 | feet | 900.5 | 591.7 |  |  | J/(lb-C) | Southwire
ACSR | Rail | 954 | 45 | 7 | 0.1456 | in | 0.0971 | in | 0.2913 | in | 1.165 | in |  |  |  | 25 | C | 75 | 0.0994 | 0.1189 | 5280 | feet | 898.5 | 175.5 |  |  | J/(lb-C) | Southwire
ACSR | Cardinal | 954 | 54 | 7 | 0.1329 | in | 0.1329 | in | 0.3987 | in | 1.196 | in |  |  |  | 25 | C | 75 | 0.0982 | 0.1199 | 5280 | feet | 898.3 | 328.7 |  |  | J/(lb-C) | Southwire
ACSR | Snowbird | 1033.5 | 42 | 7 | 0.1569 | in | 0.0872 | in | 0.2616 | in | 1.203 | in |  |  |  | 25 | C | 75 | 0.0925 | 0.1105 | 5280 | feet | 973.9 | 141.5 |  |  | J/(lb-C) | Southwire
ACSR | Ortolan | 1033.5 | 45 | 7 | 0.1515 | in | 0.101 | in | 0.303 | in | 1.212 | in |  |  |  | 25 | C | 75 | 0.0922 | 0.11 | 5280 | feet | 972.8 | 189.9 |  |  | J/(lb-C) | Ratekit
ACSR | Curlew | 1033.5 | 54 | 7 | 0.1383 | in | 0.1383 | in | 0.4149 | in | 1.245 | in |  |  |  | 25 | C | 75 | 0.091 | 0.108 | 5280 | feet | 972.8 | 356 |  |  | J/(lb-C) | Ratekit
ACSR | Bluejay | 1113 | 45 | 7 | 0.1573 | in | 0.1049 | in | 0.3147 | in | 1.259 | in |  |  |  | 25 | C | 75 | 0.0859 | 0.102 | 5280 | feet | 1048.7 | 204.8 |  |  | J/(lb-C) | Ratekit
ACSS | Puffin | 795 | 22 | 7 | 0.1901 | in | 0.1056 | in | 0.3168 | in | 1.077 | in |  |  |  | 25 | C | 75 | 0.1147 | 0.1374 | 5280 | feet | 748.8 | 207.6 |  |  | J/(lb-C) | Southwire
ACSS | Cuckoo | 795 | 24 | 7 | 0.182 | in | 0.1213 | in | 0.3639 | in | 1.092 | in |  |  |  | 25 | C | 75 | 0.1141 | 0.1367 | 5280 | feet | 748.8 | 273.9 |  |  | J/(lb-C) | Southwire
ACSS | Drake | 795 | 26 | 7 | 0.1749 | in | 0.136 | in | 0.408 | in | 1.108 | in |  |  |  | 25 | C | 75 | 0.1135 | 0.1359 | 5280 | feet | 749.1 | 344.3 |  |  | J/(lb-C) | Southwire
ACSS | Mallard | 795 | 30 | 19 | 0.1628 | in | 0.0977 | in | 0.4885 | in | 1.14 | in |  |  |  | 25 | C | 75 | 0.1125 | 0.1349 | 5280 | feet | 750.7 | 483.2 |  |  | J/(lb-C) | Southwire
ACSS | Macaw | 795 | 42 | 7 | 0.1376 | in | 0.0764 | in | 0.2292 | in | 1.055 | in |  |  |  | 25 | C | 75 | 0.1157 | 0.1385 | 5280 | feet | 749 | 108.6 |  |  | J/(lb-C) | Southwire
ACSS | Tern | 795 | 45 | 7 | 0.1329 | in | 0.0886 | in | 0.2658 | in | 1.063 | in |  |  |  | 25 | C | 75 | 0.1153 | 0.139 | 5280 | feet | 748.6 | 146.1 |  |  | J/(lb-C) | Southwire
ACSS | Condor | 795 | 54 | 7 | 0.1213 | in | 0.1213 | in | 0.3639 | in | 1.092 | in |  |  |  | 25 | C | 75 | 0.1141 | 0.1406 | 5280 | feet | 748.4 | 273.9 |  |  | J/(lb-C) | Southwire
HD Copper |  | 500 | 19 |  | 0.1622 | in |  |  |  |  | 0.811 | in |  |  |  | 20 | C | 100 | 0.11825 | 0.14953 | 5280 | feet |  |  | 1544 |  | J/(lb-C) | Old Pjm
HD Copper |  | 1000 | 37 |  | 0.1644 | in |  |  |  |  | 1.1508 | in |  |  |  | 25 | C | 75 | 0.064 | 0.0744 | 5280 | feet |  |  | 3088 |  | J/(lb-C) | Southwire

## conductor spec
Conductor Spec | normal temperature rating | normal temperature rating units | emergency temperature rating | emergency temperature rating units
AAAC | 95 | C | 135 | C
AAC | 85 | C | 110 | C
AACSR | #N/A | C | #N/A | C
AACTW | #N/A | C | #N/A | C
ACAR | 100 | C | 100 | C
ACCC | 200 | C | 200 | C
ACCR | 200 | C | 200 | C
ACSR | 140 | C | 140 | C
ACSRTW | 140 | C | 140 | C
ACSS | 250 | C | 250 | C
ACSSTW | 250 | C | 250 | C
HD Copper | 85 | C | 120 | C
Alumoweld | #N/A | C | #N/A | C